## Slide 1: A Primer on Pumps Shenandoah Valley December 2, 2015

## Slide 2
PUMP CURVES

## Slide 3: Typical Manufacturer’s Performance Curve
Selection point from pump mfr’s software
Max impeller cut
Min impeller cut
Performance curve for selected impeller cut
NPSH3 curve for selected impeller cut Power curve for selected impeller cut

## Slide 4: How a Pump Works with System Curves
Intersection of system curve and pump H/Q curve determines operating condition

## Slide 5
Best Efficiency Point
Peak wet weather flow 2300 gpm = 62 %
70 % speed proposed typical operation = 24%
NSS = 8080, Ns = 1850
Policy

## Slide 6: How a Pump Works
POR
AOR
AOR
BEP
70%
120%
Manufacturer’s minimum safe flow
POR**
AOR
AOR
**Limits of POR will depend upon on Ns and Nss
Tread very lightly here

## Slide 7: DETERMINE THE PREFERED OPERATING RANGE

## Slide 8: NPSH3 and Suction Specific Speed
Suction Specific Speed, Nss
n(QBEP)0.5
NPSH3BEP0.75
Nss = 5,000 – 10,000
Specific Speed - Ns
n(QBEP)0.5
TDHBEP0.75

## Slide 9: Pump Types – Specific Speed

## Slide 10: Stability and Suction Specific Speed (Nss)
Source: Centrifugal Pumps/Design and Application, Lobanoff and Ross 1992
nss

## Slide 11: Ns, Nss, Stability and Pump Clogging
Source: ‘Suction Specific Speed and Wastewater Pumps’ Dr. J. Evans, Pumps and Systems, Nov. 2011
Volute type
Column type
10,000 Nss Limit

## Slide 12: Principles that Promote Reliability, Efficiency and Reduced Operating Cost
Construction
  Equipment Selection
  Installation Design and Details
  Operational Controls
  Machine health monitoring

## Slide 13: Pump Structure

## Slide 14
Shaft
Thrust Bearing
Bearing Frame
Radial Bearing
Shaft Seal
Impeller
Casing
Radial load imposed
By differential pressure
Mechanical Seals: 0.002” Max Deflection

## Slide 15
Overhung Shaft
Between Bearings

## Slide 16
BEP
Shaft Seal
Increasing
Radial thrust
Radial Thrust

## Slide 17: Cavitation

## Slide 18: Misleading Pump Terminology
Net Positive Suction Head Available (NPSHA)
  The energy in feet of head, adjusted for liquid vapor pressure, in the pumped fluid at the eye of the impeller
Net Positive Suction Head Required, NPSHR,(now NPSH3)
  The energy, in feet of head adjusted for vapor pressure, in the pumped fluid at the eye of the impeller resulting in a 3 percent reduction of developed head for a given flow

## Slide 19: Mechanics of Cavitation – Recirculation
Discharge recirculation
Suction recirculation

## Slide 20: Recirculation Cavitation Damage

## Slide 21: Mechanics of Cavitation – V Cloud Cavitation Caused by Poor Impeller Vane/Cutwater Angles

## Slide 22: Bad Things Begin to Happen when Operating in the AOR…
POR
Increasing
radial thrust
Increasing
vibration
Increasing suction
recirculation Increasing inlet
surging
Increasing discharge recirculation
Increasing
cavitation

## Slide 23: Relationship Between Head, Capacity, NPSHA and Cavitation
NPSHR(3)
NPSHR(3)

## Slide 24: Operating Domains for Cavitation
NPSHi/Q
Efficiency/Q Head/Q
NPSHr/Q (- 3% H)
QBEP
Head
Efficiency
NPSH
Flow, Q
Source: “Cavitation: How Does It Happen?”
Dr. Paul Cooper, Pumps and Systems, June 2002, pg 16

## Slide 25
Incipient cavitation
Source: NPSH for Rotodynamic Pumps: a reference guide
Europump, Elsevier Science, Inc., 1999
Q

## Slide 26: WET WELLS and Pump Intakes

## Slide 27: Sources of Air in Pumped Fluid
Cascade Discharges into Wet Well from Tributary Sewers
Poor Wet Well Design
Pump Inlet Design
Wet Well Level Controls

## Slide 28: Air Trivia
Bubble rise rate ≤ 1 ft/second
Pump inlet velocity ≥ 4 ft/second

## Slide 29: Effect of Air in Pumped Fluid
Vibration
Loss of Pump Capacity

## Slide 30: Features of a Bad Pump Intake
Floor Currents
Rotating Flow
Cascades
High Energy Currents
Unconfined Inlets

## Slide 31: Features of a Good Pump Intake
The pumped fluid must approach symmetrically; no changes in direction
No high energy currents
Minimal entrained air
Sufficient NPSH margin
Intake level must be high enough to prime the pump
Sufficient submergence to avoid vortex development
Confined to prevent rotation

## Slide 32: Elimination of Air Core Surface Vortex Before and After Confined Inlet
Before Modification Modified Intake

## Slide 33: Rules for Design of Pump Intakes
No sudden reductions or expansions
Uniform approach conditions 5 diameters upstream from pump connection
No flow disturbing fittings upstream
Uniform velocity distribution at pump connection
Max velocity 8+ft/sec

## Slide 34: Traditional Wet Well Configuration
Non-uniform velocities
Swirling
Subsurface and surface vortices

## Slide 35: Traditional Wet Well Configuration (cont.)
Intakes
Inlet
Intakes
Inlet
Intake s
Intakes

## Slide 36: Confined Inlets
D
2D
22D
2.5D
3D
0.25D
0.5D
Section
Plan

## Slide 37: Trench Wet Well Advantages
Confined inlet reduces long- term wear and tear from vibration, cavitation and torque reversals caused by floor currents and vortices
Reduces vortex formation
Even load on pump bearings and seals
No screening necessary in most installations

## Slide 38: Self-Cleaning Trench-Type
Can be used for both variable speed and constant speed pumps

## Slide 39: Small Self-Cleaning Wet Wells – The Difference is in the Pump Intake
Flat Bottom; no nozzles
Shaped Bottom; nozzles

## Slide 40: Pump Foundations

## Slide 42: Foundations Are Important

## Slide 43: The Result

## Slide 44: Questions?